LOWER VALLEY FIRE PROTECTION DISTRICT

168 N. Mesa

Fruita, CO. 81521

Phone: (970) 858-3133 Fax: (970) 858-7189

The Event Organizer must obtain a permit from the Fire department at least 30 days prior to the event.

SAFETY REQUIREMENTS FOR TEMPORARY EVENTS

- Tent fabric and /or canopies: Shall meet the requirements for flame resistance in accordance with National Fire Protection Association Standard 701 or California State Fire Marshal Standard. A permanent affixed label bearing the identification and fabric, or material type is required. Certification from recognized agencies or testing facilities will be accepted. Exception: Tents not exceeding 144 square feet, canopies open on all sides not exceeding 200 square feet and which do not contain cooking or heating appliances.

- Means of Egress from tents or Canopies: No guy wire or guy rope shall cross any means of egress from any tent open to the public at a height of less than 7 feet. Tent stakes adjacent to any means of egress shall be railed off, capped, or covered so as not to present a hazard to the public.

- No smoking, open flames or heating devices allowed in tents or booths (except cooking booths).

- Electrical cords: Extension cords shall be rated for at least “junior hard service per the Electric Code. An example is “SJO”.  Cords shall be grounded and protected by a GFCI. Cords shall not be in contact with metal fences. Cords shall be protected from traffic and located /protected to prevent a tripping hazard. All electrical service and wiring shall comply with the National Electric Code.

- Cooking Booths: All cooking devices shall be isolated from the general public by not less than 48 inches or must be protected by barriers between the devices and the public. Cooking equipment shall be kept a horizontal distance of not less than 24 inches from any combustible material. Each cooking booth shall have at least one exit-way, a minimum three feet wide and 6’ 8” high. Booth frame shall not obstruct exit pathway. Cooking booths shall have a minimum clearance of ten feet on at least two sides and be at least ten feet from any vendor booth or building Mobile food preparation vehicles that are equipped with appliances that produce grease or smoke shall meet the requirements of Sections 319 and 607 of the 2018 IFC for fire protection and ventilation.

- Fire Extinguishers: At least one fire extinguisher with a minimum U.L. rating of 2A:10BC shall be in each tent or facility.  A Class “K” fire extinguisher is also required for any cooking operation that uses a deep fat fryer. Note: All extinguishers must have a current annual inspection tag or sticker attached.

- LP GAS Cylinders: All LP gas cylinders shall be secured in an upright position (not to a tent support) and be located not less than 10 feet from any tent, cooking operation or heating device. Cylinders shall be protected from vehicle traffic and the relief valve shall be pointed away from any tent, building, other cylinders or ignition source(s).  Trash and other combustible material shall be kept a minimum of 10 feet from LP gas tanks and containers. Shut valves when gas is not in use.

- Shavings, hay and straw bales: No bales, shavings or saw dust shall be located within any tent or within 10 feet thereof.

- . No solid fuel grills allowed (Hibachi, etc.). Solid fuels include charcoal, wood.

- Generators shall be separated from booths by a minimum of five (5) feet and protected from contact by fencing or other approved means. Fuel tanks shall have adequate capacity to permit uninterrupted operation during normal operating

hours. Extra fuel shall be stored in an UL or FM approved safety can.

- The use of Tiki Torches and Sky Lanterns is prohibited.

- Events Exiting Requirements for fenced or secured areas:

The number of exits, exit width, and spacing shall be determined and approved by the Fire Marshal.   Minimum requirements shall be as follows:

- . A minimum of two exits shall be provided.

- . Three exits shall be provided when the site contains from 1,000 to 3,000

persons.

- . Four exits shall be provided when the site contains more than 3,000

persons.

- . Exits shall be spaced so that no exit is greater than 400 feet of travel.

Additional exits shall be added if needed.

- . Exits width shall be a panel width of temporary fencing, to provide an

opening of no less than six feet clear width.

- . Each exit shall have a member of the event staff assigned to it.

- . Exit signs shall have a white background with contrasting letters. Exit   signs shall measure no less than 18 x 24 inches, sign lettering shall measure 12 inches in height with a minimum of 1 ½ wide letters.

- Exit Signs shall be placed at the top center of exit panels.

- Emergency vehicle access: A fire lane designated by the fire department of not less than 20 feet width and no overhead obstructions lower than 13 feet 6 inches shall be maintained. Blocked main streets and cross streets shall have Emergency vehicle access. Signs shall be provided designating Fire Access/ No Parking. Standard Fire Lane/ No parking signs may be used.

Access to fire hydrants, FDC’s, building entrances shall not be obstructed in any manner. 15 feet clear on each side of a fire hydrant.

- The Event Organizer shall provide a site plan to the Fire Marshal showing the following:  Name of all streets and areas included in the event. Location(s) of Fire Department Access Lanes. Location of stages, vendors, display areas; location of Emergency Exits if event is fenced.

- The Event Organizer shall distribute to each vendor a copy of this document prior to the event.

Revised 5/13/20. Ref: 2018 IFC, Chapter 3,9 & 31 of the IFC & NFPA 1, Chapter 25.